## COVER
DD FORM 1391 COST ESTIMATE
Building | SCH-3270
iNFADS Description | AUTO ORGANIZATIONAL SHOP CAB
Primary CCN | 21451
RPUID | 1174058
PAX ID | 387568
Fi Web Project Number | BU26PPE74M
Installation/UIC | M67400 (SH)
Location | MARINE CORPS BASE, CAMP SMEDLEY BUTLER (CAMP SCHWAB-6009), HENOKO OKINAWA, JAPAN
Project Title | Repair Bldg. 3270
Fund Type | O&MMC
Acquisition Method | Design-Build (DB)
Total Building GSF (iNFADS) | 25390
PRV (iNFADS) | 39507617
LSH (2.5% of PRV) | 987690
Locked Total Project Cost ($) | 3527753
Locked TPC ($000, printed) | 3528
Prepared By | Anthony L. Potter, Facilities Planner, MCIPAC G-F PPE
Signing Officer (PWO) | CDR Justus K. O'Connor
Government Client | Bil Hawkins, P.E., PMP, Deputy PWO
Reviewer | Robert W. Kaye, RA, Planning Director NAVFAC FEAD

## BLOCK9
9. Cost Estimates
Item | UM | Quantity | Unit Cost | Cost ($000)
PRIMARY FACILITY
AUTO ORGANIZATIONAL SHOP CAB FAC#3270 (Conversion / Alteration) | SF
Subtotal
Contingency (10.0%)
Total Contract Cost
Supervision, Inspection and Overhead (8.0%)
Total Funded Cost
Design-Build - Design Cost (4.0%)
TOTAL PROJECT COST
Planning and Design (6.0%) (NON ADD)
Equipment from Other Appropriations (NON ADD) |  |  |  | 0
Classification of Work
Construction
Special Interest Codes
Restoration and Modernization

## BLOCK10
10. Description of Proposed Construction
The building serves as the primary automotive organizational shop for 4th Marine Regiment (4th MarRegt) and Combat Logistics Battalion 4 (CLB-4) on Camp Schwab. Following completion of this project, the building will remain in operational use for a minimum of 20 years. This project provides for the repair by replacement of the facility's failing mechanical, electrical, and life safety systems, correction of moisture-related architectural deficiencies, modernization of the telecommunications infrastructure, and installation of a mass notification system across both floors to meet current operational requirements, network standards, and UFC compliance. Minor deficiencies identified during the project scope will also be repaired. The project also replaces end-of-life exhaust systems, repairs plumbing safety stations, and addresses exterior door serviceability. MECHANICAL: The project will replace all seven existing HVAC split unit systems and 24 associated indoor fan coil units throughout the facility. New split unit HVAC will be installed in the first and second floor hallways. The air-exchange infrastructure will be redesigned to improve building-wide air circulation, including replacement of ventilation components, evaluation and right-sizing of fan power, and installation of door louvers. All four direct outdoor air supply units serving administrative areas will be replaced. Twenty-two exhaust fans serving restrooms, shops, mechanical rooms, and maintenance bays will be replaced. Ten vehicle exhaust hose reel assemblies in the maintenance bays will be replaced. The abandoned dust collection system in the Wood Shop will be fully removed. The welding exhaust system in the Welding Shop, including fans, roof ventilator, exhaust hood, and associated ductwork, will be repaired and restored. The battery room ventilation and conditioning system will be upgraded to meet code requirements. The compressed air system will be inspected, pressure-tested, and repaired as necessary. ELECTRICAL: All high-bay overhead lighting fixtures will be replaced throughout the facility, including 62 EA standard high-bay fixtures and 30 EA 400-watt metal halide fixtures requiring lift and rigging. All motion sensor-capable and optically- sensored lighting fixtures will be replaced. Electrical panel work, circuit modifications, and branch wiring associated with fixture replacement will be performed on both floors. ARCHITECTURAL: Replace mold/mildew-affected ceiling tile. Repair gypsum and concrete wall damage. Resecure exterior HVAC anchor cables. Remediate restroom mold/mildew. COMMUNICATIONS: New Category 6 infrastructure will be installed throughout the facility according to the current MCIPAC G-6 policy. Both telecom rooms are included in scope. Seventy NIPR network drops will be installed to support 4th Marine Regiment and CLB-4 operational requirements. CYBERSECURITY: The project's design and construction shall fully address Facility- Related Control Systems (FRCS) cybersecurity requirements, to include cybersecurity commissioning. These requirements are in accordance with current Department of Defense (DoD) criteria, Unified Facilities Criteria (UFC) standards, and National Institute of Standards and Technology (NIST) guidelines. Cybersecurity features include hardware, software, documentation, and testing provided by the construction contractor for FRCS. Cybersecurity commissioning covers government-provided documentation and testing for FRCS cybersecurity. PLUMBING: All emergency eyewash and shower stations will be replaced building-wide. Additional emergency shower capability will be added at maintenance bay locations currently served by eyewash only, in compliance with ANSI Z358.1 distance requirements. The second-floor electric water cooler will be replaced. LIFE SAFETY: Emergency lighting fixtures will be replaced with units incorporating integral battery backup throughout the facility. A mass notification system will be installed in compliance with applicable UFC guidelines and Fire Protection Engineering for Facilities.

## BACKUP
BACKUP - Locked TPC back-solver (drives BLOCK9 face)
INPUTS (locked)
Locked TPC ($) | 3527753
GSF (iNFADS, locked Quantity) | 25390
PRV ($, iNFADS) | 39507617
LSH ($, 2.5% of PRV)
Multiplier (1.10 x 1.08 x 1.04) | 1.2355
PAX ENTRY (what Anthony types into Block 9)
Unit Cost ($/SF)
Items Table Subtotal (raw $) = GSF x UC
Items Table Subtotal ($000)
PAX ROLLUP (computed from items table subtotal)
Subtotal ($)
Contingency (10.0%)
Total Contract Cost
SIOH (8.0%)
Total Funded Cost
Design-Build Design (4.0%)
Total Project Cost ($)
Total Project Cost ($000)
Planning and Design (6.0%) (NON ADD)
RECONCILIATION
Workbook TPC ($)
Locked TPC ($)
Delta ($)
Workbook TPC ($000)
Locked TPC ($000, printed)
Delta ($000) - MUST BE 0

## RATES
RATES (PAX Associated Costs and project parameters)
PAX Associated Costs (pre-loaded by operator)
Contingency | 10% | FSRM program-directed; CRB Guidelines May 2024 (REV #15)
Supervision Inspection and Overhead (SIOH) | 8% | OCONUS FSRM customer-directed for MCIPAC G-F
Design Build (DBD) - REQUIRED | 4% | UFC 3-730-01 (2024) - applied after Total Funded Cost
Planning and Design (P&D) (NON ADD) | 6% | Does not roll into TPC
Project parameters
Area Cost Factor (ACF) | 1.85 | UFC 3-701-01 w/Change 7 (25 Jul 2025), Table 4-1, M67400-0004 OCONUS Okinawa
LSH Rate (% of PRV) | 2.5% | Local direction at startup
JPY/USD Planning Rate | 150.4415 | FY26 budget planning rate
JPY/USD H.10 Rate (live) |  | Verify Federal Reserve H.10 on date of PAX submission
Escalation (annual) | 2.1% | OSD FY25 published rate
General Requirements | 10% | FSRM program-directed

## REFERENCES
REFERENCES (authority cites)
Document | Date / Edition | Authority for
MCO 11000.5 | 03 Jun 2016 | Real Property FSRM Program
MCO 11000.12 | 08 Sep 2014 | Real Property Facilities Manual
CRB Guidelines (REV #15) | May 2024 | Block 9 line-item sequencing
UFC 3-701-01 with Change 7 | 25 Jul 2025 | PUC and ACF tables, Equation 3-1 PRV formula
UFC 3-730-01 | 2024 | Design-Build contracting; DB Design 4% applied after TFC
JED Cost Estimating Guide | Nov 2025 | Cost estimating methodology
Japan District Design Guide v9 | April 2025 | Okinawa-specific design criteria
NOT CITED
NAVFAC 11010.44E | INACTIVE | Inactivated by 1987 issuance; not citable